Bates Hall Building Biography

A. Structural Facts

Construction Type    2C

Occupancy Group:    A-3 – Music Room;  A-4  - Classrooms

Year Built:                1961

Height:                      36 ft (including basement)

Area:                         49,474 s.f.     Tabular: 16,254

Foundation Type       Concrete spread footings

Floor / Ceiling:          Concrete slab/ VCT and Carpet

Roof:                         Concrete waffle           Built up T&G

Exterior Walls           Masonry – Concrete Block, brick veneer

Interior Finish           Painted concrete block; hallways and bathrooms ceramic tile

Fuels                         None in building (Heat and hot water supplied by Power Plant)

Natural Gas – see generator

Heat                          Supplied by Power Plant (#4 Oil, PH Steam)

Hot Water                 Supplied by means of instantaneous HPS tankless system located in

Parenzo/Scanlon Utility Tunnel

Ventilation               Classroom: Univents, Bathrooms; Roof top exhaust hoods. Basement

partially serviced by central air conditioning. Remainder services by

windows.

Electrical Service      4160  vac 3 phase supplied from Power Plant reduced to 208 vac.

Emergency Light      Hallway and corridor lights supplied from emergency generator

Emergency Power    1 generator: 100kw @ 120/208vac, diesel. Supplied emergency

lights fire alarm

Fire Alarm Equip     Simplex 2001; hallway pull stations at exits only

Suppression              Standpipes at hallway extinguisher cabinets (Insp. By WSC empl)

Smoke Evacuation    None

Extinguishers            2 H2O;  3 ABC; 1 BC. Inspected and tested annually by Atwood

Fire Equipment Co.

Chimneys                 1 incinerator and ceramic spark arrestor flue (inactive)

Elevator                    1 installed 2007

Shafts/Atria              Utility pipe chases                        .

Emergency evacuation signs:

Septic                        Municipal

Water                        Municipal

Certificate

B. Building Upgrades

2007

1. New Elevator installed

2. New glass entry area

3. New student lounge over entry ( floor 1 ½)

2008

New Carpet in rooms: 24, 07, 103, 114, 127